## Slide 1: Residual Current Monitor Ongoing Projets

## Slide 2: Residual Current protective Device (RCD) vs. RCM
L2
L3
N
L1
L2
L3
N
L1
to the load
to the grid
I >
Test button
Electromagnetic release
Circuit braker
Summation current transformer
L2
L3
N
L1
L2
L3
N
L1
to the load
to the grid
Summation current transformer
Test button
Monitoring with evaluation unit
PE
PE

## Slide 3: RCM in TN-S systems
Load 1 with frequency converter / switched-mode power supply
R iso C1
R iso C1
Load 2 with frequency converter / switched-mode power supply
R iso C2
By measuring the current in the central earthing point (CEP), the insulation of the entire system can be assessed.
L2
L3
N
L1
PE
CEP-measuring The entire leakage current of the system flows here.
Ires C1
Ires C2
Ires ∑
R iso L1
R iso L2
R iso L3
PEN conductor from transformer
Measurement processing
Universal Measurement Device:
1 x 4-Phase-Voltage Measurement
X x inputs for current measurements (Energy measurement)
X x inputs for residual current measurements
Ires ∑
R iso C2
R iso N
Current sensors for energy measurement

## Slide 4: GE 5 MW Wind Energy Plant
Pitch system
Turns blades out of the wind to control rotor speed. Also, stops the rotor from spinning in conditions where wind blowing too slow or too fast

## Slide 5: SRCMH070IB+
Master thesis in cooperation with Beckhoff Automation
gravel plant separator
Energy Residual Current

## Slide 6: Monitoring using 4-20 mA output (1000 ms)
Chart: Residual Current
Due to the integration interval over 1000 ms, the current peaks during switch-on and switch-off processes are smoothed, so that no clearly increased values are recognizable via the TRMS calculation.

## Slide 7: Permitted residual current levels of equipment
Rated current of current-using equipment a.c. | Maximum protective conductor current for frequencies up to 1 kHz
0 < I ≤ 2 A | 1 mA
2 A < I ≤ 20 A | 2.5 mA/A
I > 20 A | 10 mA
Maximum levels of current on the protective earth conductor of equipment and loads in normal operation up to 1 kHz
Rated current of current-using equipment a.c. | Maximum protective conductor current d.c.
0 < I ≤ 2 A | 5 mA
2 A < I ≤ 20 A | 2.5 mA/A
I > 20 A | 50 mA
Since DC residual currents can also occur in many loads such as frequency converters, there is the following version to read under 7.6.3.4.
…In normal use, a.c. current using equipment shall not generate current with a d.c. component in the protective conductor that exceeds the values in in following table. This will prevent affecting the proper functioning of protective device(s) or other equipment in the installation. …
In international standardization, the standard IEC 61140:2016 under point 7.6.3.3 defines the maximum levels of current on the protective earth conductor of equipment and loads in normal operation up to 1 kHz.
IEC 61140, Revision 4.0, January 2016 - Protection against electric shock – Common aspects for installations and equipment
Laboratory Measurements

## Slide 8: Just a question!
Do you have type A RCDs at your facility?
Do you need type B? Check it out! You have only one life!

## Slide 9
Thank You